Fusion Module 500 Checklist

Verifying the Installation

Notes: Fill the following information, implementation company and final customer has to sign, scan and share with Huawei.

At least one photo has to be taken for each point in the following list to validate is already done.

Share with 7 days in advance before the startup date to assign Huawei engineers on time.

Check list Guide to validate Installation

| Category | Check Item | Check Result | Photographic evidence |
| --- | --- | --- | --- |
| Validation | I declare that the entire installation is done and the equipment will have energy to do the start up. In opposite case the visit of Huawei engineers will count as complete service. | □Yes □No |  |
|  | The equipment is entirely installed by certified people and following the Huawei installation manual with EHS and quality standards. | □Yes □No |  |
| Cabinet | The cabinet position is consistent with the equipment room layout diagram. | □Yes □No | Photo |
|  | All bolts and screws are firmly tightened, especially on electrical connections. Flat and spring washers are used with each bolt, and spring washers are placed on the top of flat washers. | □Yes □No | Photo |
|  | The cabinet is clean and complies with dustproof requirements. | □Yes □No | Photo |
|  | All labels are correct, clear, and complete. | □Yes □No | Photo |
|  | The paint on the cabinet exterior is intact. If paint flakes off, repaint that area immediately to avoid corrosion. | □Yes □No | Photo |
|  | The cabinet doors and locks work properly. | □Yes □No | Photo |
|  | There are no sundries such as adhesive tape, cable tie, paper scrap, or packing material around the cabinet. | □Yes □No | Photo |
|  | All components are properly installed and no component is left onsite. | □Yes □No | Photo |
|  | Idle cable holes are completely cover with the sealing putting. | □Yes □No | Photo |

| Cable | All cable joints are secured properly, especially the cable joints of network cables. | □Yes □No | Photo |
| --- | --- | --- | --- |
|  | Exposed parts of cables and cable lugs near the cable terminals are wrapped with insulation tape or heat-shrink tubing. | □Yes □No | Photo |
|  | Flat washers and spring washers of all wiring terminals are securely installed and in good contact. | □Yes □No | Photo |
|  | Cables are bound neatly, and cable ties are secured evenly and properly in the same direction. | □Yes □No | Photo |
|  | Excess sections of cable ties are neatly cut. | □Yes □No | Photo |
|  | There is no unnecessary adhesive tape or cable tie on cables. | □Yes □No | Photo |
|  | Cables are routed in a way convenient for maintenance and future capacity expansion. | □Yes □No | Photo |
|  | Labels at the cable ends are clear. | □Yes □No | Photo |
| Electrical connection | All ground cables are copper cables with diameters meeting the requirements. No switch or fuse is installed on a ground cable, and no open circuit occurs. | □Yes □No | Photo |
|  | All ground cables, AC input cables, and intra-cabinet cables are connected correctly according to the power system circuit diagram, and all screws are fastened. The input and output cables are not short-circuited. | □Yes □No | Photo |
|  | The smart cooling product input voltage is within the range of rated voltage ±10%, and the input frequency is within the range of rated frequency ±3 Hz. | □Yes □No | Photo |
|  | Power cables and ground cables are not coiled and excess parts are cut off. | □Yes □No | Photo |
|  | Lugs for power cables and ground cables are welded or crimped securely. | □Yes □No | Photo |

| Electrical connection | Power cables and ground cables are routed and bound separately from other cables. | □Yes □No | Photo |
| --- | --- | --- | --- |
|  | Batteries are intact, free from damage, cracks, and bulges. | □Yes □No | Photo |
|  | Batteries are neat and clean, and do not leak electrolyte. | □Yes □No | Photo |
|  | Battery terminals are upright and free from damage, break, and acid leakage. | □Yes □No | Photo |
|  | Battery cables are connected correctly. | □Yes □No | Photo |
|  | DIP switches on devices are correctly set. | □Yes □No | Photo |
|  | Verify the correct phase sequence with a proper tool. | □Yes □No | Photo |
|  | According with the model and manual specifications about the equipment input voltage, assure the accurate breaker input and output. | □Yes □No | Photo |

We declare all materials, installation and connections was done following the "FM500 Data Center User Manual" and according with site specifications, following the local regulations.

__________________________________

Partner approval

Name Company name Job Position