
Fusion Module 500 Checklist



Verifying the Installation



       Notes: Fill the following information, implementation company and final customer has to sign, scan and share with Huawei.
At least one photo has to be taken for each point in the following list to validate is already done.
Share with 7 days in advance before the startup date to assign Huawei engineers on time.


































Check list Guide to validate Installation
	Category
	Check Item
	Check Result
	Photographic evidence

	Validation
	I declare that the entire installation is done and the equipment will have energy to do the start up. In opposite case the visit of Huawei engineers will count as complete service.
	□Yes □No
	

	
	The equipment is entirely installed by certified people and following the Huawei installation manual with EHS and quality standards.
	□Yes □No
	

	Cabinet
	The cabinet position is consistent with the equipment room layout diagram.
	□Yes □No
	Photo

	
	All bolts and screws are firmly tightened, especially on electrical connections. Flat and spring washers are used with each bolt, and spring washers are placed on the top of flat washers.
	□Yes □No
	Photo

	
	The cabinet is clean and complies with dustproof requirements.
	□Yes □No
	Photo

	
	All labels are correct, clear, and complete.
	□Yes □No
	Photo

	
	The paint on the cabinet exterior is intact. If paint flakes off, repaint that area immediately to avoid corrosion.
	□Yes □No
	Photo

	
	The cabinet doors and locks work properly.
	□Yes □No
	Photo

	
	There are no sundries such as adhesive tape, cable tie, paper scrap, or packing material around the cabinet.
	□Yes □No
	Photo

	
	All components are properly installed and no component is left onsite.
	□Yes □No
	Photo

	
	Idle cable holes are completely cover with the sealing putting.
	□Yes □No
	Photo



	






	Cable
	All cable joints are secured properly, especially the cable joints of network cables.
	□Yes □No
	Photo

	
	Exposed parts of cables and cable lugs near the cable terminals are wrapped with insulation tape or heat-shrink tubing.
	□Yes □No
	Photo

	
	Flat washers and spring washers of all wiring terminals are securely installed and in good contact.
	□Yes □No
	Photo

	
	Cables are bound neatly, and cable ties are secured evenly and properly in the same direction.
	□Yes □No
	Photo

	
	Excess sections of cable ties are neatly cut.
	□Yes □No
	Photo

	
	There is no unnecessary adhesive tape or cable tie on cables.
	□Yes □No
	Photo

	
	Cables are routed in a way convenient for maintenance and future capacity expansion.
	□Yes □No
	Photo

	
	Labels at the cable ends are clear.
	□Yes □No
	Photo

	Electrical 
connection
	All ground cables are copper cables with diameters meeting the requirements. No switch or fuse is installed on a ground cable, and no open circuit occurs.
	□Yes □No
	Photo

	
	All ground cables, AC input cables, and intra-cabinet cables are connected correctly according to the power system circuit diagram, and all screws are fastened. The input and output cables are not short-circuited.
	□Yes □No
	Photo

	
	The smart cooling product input voltage is within the range of rated voltage ±10%, and the input frequency is within the range of rated frequency ±3 Hz.
	□Yes □No
	Photo

	
	Power cables and ground cables are not coiled and excess parts are cut off.
	□Yes □No
	Photo

	
	Lugs for power cables and ground cables are welded or crimped securely.
	□Yes □No
	Photo




	Electrical 
connection

	Power cables and ground cables are routed and bound separately from other cables.
	□Yes □No
	Photo

	
	Batteries are intact, free from damage, cracks, and bulges.
	□Yes □No
	Photo

	
	Batteries are neat and clean, and do not leak electrolyte.
	□Yes □No
	Photo

	
	Battery terminals are upright and free from damage, break, and acid leakage.
	□Yes □No
	Photo

	
	Battery cables are connected correctly.
	□Yes □No
	Photo

	
	DIP switches on devices are correctly set.
	□Yes □No
	Photo

	
	Verify the correct phase sequence with a proper tool.
	□Yes □No
	Photo

	
	According with the model and manual specifications about the equipment input voltage, assure the accurate breaker input and output.
	□Yes □No
	Photo





   We declare all materials, installation and connections was done following the "FM500 Data Center User Manual" and according with site specifications, following the local regulations.





            __________________________________	
	Partner approval

	Name
Company name
Job Position
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